WISI GT34 Satellite TV Technical Monitoring System

Complete Engineering, Discovery, Installation, Configuration & Commissioning Runbook

Production architecture checkpoint V11.3L | Windows / Python / PRTG / SQLite

Purpose: A from-scratch, evidence-driven procedure for an engineer who may begin with only a WISI Tangram/GT34, product documentation, and possibly vendor MIB files. It also documents the proven production architecture and the commands used by this project. It is not a vendor manual and does not invent undocumented OIDs, endpoints, enum meanings, thresholds, or device capabilities.

Prepared from the validated V11.3L project documentation and production migration source tree.

# 1. How to use this runbook

Use this document in order. Do not jump directly to PRTG sensor creation. The authoritative chain is: establish device reachability -> discover SNMP and structured web data -> establish deterministic logical-input identity -> prove service/ES scope -> build a baseline -> validate one carrier -> deploy the bounded PRTG presentation -> validate SQLite history -> configure Python alarm/email -> commission the fleet.

Evidence first: a parameter is supported only when the IRD exposes it through a verified interface or the project derives it from verified observations.

Fail closed: if a logical input cannot be mapped deterministically, do not assign an arbitrary tuner or service.

Separate identity domains: chassis/module identity, low-level tuner index, WISI GUI logical input, and DVB service SID are not interchangeable.

PRTG is a visualization/read-only layer. Python is authoritative for collection, service integrity, alarm state, duplicate suppression, recovery, and email.

SQLite is the historical system of record; TV43 carrier/service history retention is exactly 15 days.

Production PRTG schema is deliberately bounded at a maximum of 44 live channels per sensor even though EXE/Script Advanced has a 50-channel ceiling.

# 2. Proven production architecture

| Layer | Production role | Authority |
| --- | --- | --- |
| WISI GT34 / Tangram | RF demodulation, TS/service state, structured device telemetry | Source device |
| Python acquisition | SNMPv2c + structured WISI web/resource acquisition, deterministic correlation | Authoritative acquisition |
| Authoritative inventory | Logical carrier and expected DVB service identity | Authoritative identity |
| SQLite | Rich carrier/service observations and 15-day TV43 history | Historical system of record |
| PRTG EXE/Script Advanced | Stable bounded channels + rich status/message | Viewer/dashboard only |
| Python alarm policy | Carrier/TS/service-integrity episodes, suppression, recovery | Authoritative alarm logic |
| SMTP/email | Transmission Alert DOWN/UP notifications | Python-controlled; not PRTG triggers |

# 3. Starting scenarios

| Starting material | First action | Rule |
| --- | --- | --- |
| Product documentation + MIB files | Review documented SNMP capability, compile MIBs if useful, walk the live device, correlate numeric OIDs with known state. | Do not assume a MIB object is operationally populated merely because it exists. |
| Product documentation, no MIB files | Use documentation to identify expected capabilities; inspect SNMP numerically if enabled; inspect structured web-interface traffic. | Do not invent symbolic OIDs. |
| MIBs are incomplete/unhelpful | Treat GUI-visible state as evidence that the chassis can retrieve data; inspect browser Network traffic and machine-readable resources. | Prefer structured responses, not screen-label scraping. |
| Firmware/UI changed | Repeat structured request observation and compare against known carrier fingerprints before changing production mappings. | Never carry old endpoints/mappings forward without evidence. |

# 4. Workstation/server prerequisites

The validated working environment was Windows with Python 3.14.6. The project intentionally uses standard-library implementations for core runtime functions, including SQLite, SMTP/email, HTTP/XML and its internal SNMPv2c client. The GitHub project requirements file should remain the project dependency specification; a pip-freeze snapshot is reference material, not an instruction to install every package.

# PowerShell

python --version

python -m pip --version

git --version

Get-Service *PRTG* | Select-Object Name,DisplayName,Status

# From project root:

python -m pip install -r .\requirements.txt

python -c "import sqlite3, smtplib, json, xml.etree.ElementTree; print('STANDARD LIBRARY OK')"

python -c "import gt34_monitor; print('GT34 PROJECT PACKAGE OK')"

Server path: For a clean server installation use a stable path such as C:\WISI\wisi-gt34-monitor. Do not retain old user Desktop paths in PRTG wrappers or Scheduled Tasks.

# 5. Phase A - establish physical and network identity

## 5.1 Record the chassis before polling

Record chassis management IP, model, firmware/software version, installed physical slots, GT34 slots, and the known RF input/carrier configuration.

Confirm the browser GUI is reachable and that the GT34 module is shown as running.

Record at least one known carrier per GT34: frequency, polarization, symbol rate, and one known DVB service/SID if available. These become correlation fingerprints.

## 5.2 Basic network tests

Test-Connection <CHASSIS_IP> -Count 2

Test-NetConnection <CHASSIS_IP> -Port 80

Test-NetConnection <CHASSIS_IP> -Port 161

UDP caveat: Test-NetConnection is primarily useful for TCP. SNMP uses UDP/161, so the authoritative SNMP test is an actual SNMP GET/WALK or this project's SNMP client, not a successful TCP test.

# 6. Phase B - SNMP/MIB investigation from scratch

The project began as a MIB/PRTG exercise. Importing the available WISI MIB material into PRTG did not automatically expose the complete regulator-facing parameter set. The final solution therefore uses SNMP where useful and structured WISI web resources for enrichment/service identity.

## 6.1 If MIB files are available

Preserve the original vendor MIBs unchanged.

Load/compile them in an SNMP browser or PRTG MIB importer if desired, but treat this as a naming aid, not proof of live telemetry.

Perform a numeric walk and save the raw output. Numeric OIDs remain useful even if symbolic compilation fails.

Change one known device state at a time only when operationally safe; compare walk values to identify candidate objects.

Document OID, ASN.1 type, observed value, scaling/unit evidence, source MIB, and correlation confidence.

## 6.2 If MIB files are absent or not useful

Use the product documentation to understand the device, but do not convert a documented GUI field into an assumed OID. Continue with live numeric SNMP discovery and the structured web-interface workflow in Phase C.

## 6.3 Project-native SNMP configuration

# config.toml template - replace placeholders locally

[snmp]

host = "<CHASSIS_IP>"

community = "<SNMP_COMMUNITY>"

port = 161

timeout_seconds = 2.0

retries = 1

## 6.4 Project discovery commands

# Run from project root in PowerShell.

python .\tools\discover.py --config .\config.toml

python .\tools\discover_modules.py `

--config .\config.toml `

--host <CHASSIS_IP>

# Include controller/system rows if needed:

python .\tools\discover_modules.py `

--config .\config.toml `

--host <CHASSIS_IP> `

--all-components

# Discover DVB services only on physical GT34 modules:

python .\tools\discover_services.py `

--config .\config.toml `

--host <CHASSIS_IP>

# Limit to one physical GT34 slot:

python .\tools\discover_services.py `

--config .\config.toml `

--host <CHASSIS_IP> `

--module 1

# Write a candidate expected-service baseline:

python .\tools\discover_services.py `

--config .\config.toml `

--host <CHASSIS_IP> `

--write-toml .\baselines\candidate_<CHASSIS>.toml

# Complete ES/PID map for one logical input:

python .\tools\discover_streams.py `

--config .\config.toml `

--host <CHASSIS_IP> `

--module 1 `

--channel 1

PYTHONPATH: When invoking scripts under tools from unusual shells or copied locations, the project root must be importable. Normally run from the project root. If Python cannot import gt34_monitor, set $env:PYTHONPATH=(Get-Location).Path for that PowerShell session and retry.

# 7. Phase C - discover the WISI web-interface data path

This phase is foundational. The successful implementation did not rely on screen scraping. It observed the structured HTTP/XML/resources used behind the WISI/Tangram GUI's GT34 module/input/status/service views and correlated those responses with known tuning and SNMP observations.

## 7.1 Browser procedure

Open the chassis web interface and authenticate using the site's normal administrative procedure.

Open browser Developer Tools -> Network. Preserve the log while navigating.

Navigate to a known GT34 module, then a known logical input, status view, transport/service view, and any elementary-stream/PID view.

Filter Network traffic for XHR/fetch/XML/HTTP requests. Record request method, path, query/body, response content type, and a small redacted response sample.

Switch to another known logical input. Compare which request fields/path components change and which response fields track frequency, symbol rate, lock, RF/SNR, TS/service identity or ES/PID data.

Repeat on a second chassis/module before declaring a request pattern generic.

Correlate each candidate response to a known carrier fingerprint. Frequency + polarization + symbol rate + service identity is stronger evidence than a tuner index alone.

Preserve evidence in a discovery log. If the firmware/UI changes later, repeat this procedure rather than guessing old endpoints.

Known path form: Historical GUI-style logical paths included /remote/<logical-remote>/. A newer 169.254.x.x transport/module binding must not be substituted for a GUI logical remote without evidence. Exact undocumented endpoint names that were not preserved as evidence are deliberately not fabricated in this runbook.

## 7.2 Project modules implementing the correlation

| Component | Role |
| --- | --- |
| gt34_monitor/webstatus.py | Structured WISI web-status acquisition and deterministic/fail-closed logical mapping. |
| gt34_monitor/fastpath.py | Fast polling/enrichment path combining device observations with web data. |
| gt34_monitor/prtg.py | PRTG-oriented presentation logic used by the older structured path. |
| prtg_sensor.py | One logical-input PRTG sensor interface; supports host/baseline overrides. |
| tools/discover_services.py | GT34 service discovery and candidate baseline generation. |
| tools/discover_fleet.py | Fleet-wide configured-IRD discovery. |
| tools/discover_streams.py | Service-level elementary-stream/PID mapping. |
| baselines/baseline_<host>.toml | Per-host approved logical/service expectation baseline. |

## 7.3 Fail-closed mapping rule

The mapping must not fall back to an arbitrary tuner when the web response cannot be correlated. The v1.3 logic specifically treats non-positive SNMP LO frequency as unavailable rather than as a literal 0 kHz LO; when LO is unavailable, matching still requires the nominal tuner/channel relationship, healthy web lock, SNR consistency, RF-level consistency, and exactly one matching internal remote.

A match is accepted only when the evidence uniquely identifies the intended logical input.

Ambiguous/no match -> report unavailable/mapping failure; do not manufacture values.

Low-level tuner IDs 0-7 are not the authoritative logical catalogue; the proven GUI inventory contains logical channel numbers above 8.

# 8. Phase D - build an authoritative logical inventory

For a new deployment, discovery output must be converted into an approved inventory before PRTG deployment. In the validated production fleet, Inventory V6 proved 74 logical inputs, 43 active TV-bearing carrier inputs, 168 DVB service instances, and zero service-count mismatches. Those counts are deployment-specific examples, not universal GT34 limits.

# Fleet discovery

python .\tools\discover_fleet.py --config .\config.toml --list-only

python .\tools\discover_fleet.py --config .\config.toml

# Restrict discovery to one configured host during commissioning

python .\tools\discover_fleet.py `

--config .\config.toml `

--host <CHASSIS_IP>

## 8.1 Approval criteria for each logical carrier

Chassis and physical GT34 module are known.

Logical channel/input identity is deterministic.

Frequency, polarization and symbol rate agree with the intended carrier where exposed.

Current TS/service discovery is available.

Expected SIDs/service names are reviewed; service identity is SID-based, not name-only.

TV-bearing classification is evidence-based: at least one expected service has explicit video ES/PID evidence. Do not infer television versus radio from the service name.

If a service is present but ES metadata is unavailable, record ES-N/A; do not claim black/off-air decoded video.

# 9. Phase E - parameter acquisition and presentation matrix

The system intentionally separates acquisition from presentation. Not every acquired field becomes a PRTG channel. The bounded channel surface is for operational visualization; richer data remains in status text and SQLite.

| Parameter/family | Acquisition/derivation | PRTG | SQLite/history | Operational meaning |
| --- | --- | --- | --- | --- |
| Carrier / TS Health | Derived from lock + TS state | Core channel | Yes | Top-level carrier/TS state |
| Demod Lock | IRD structured observation | Core channel | Yes | RF demodulator lock |
| Transport Stream Present | IRD structured observation | Core channel | Yes | TS availability |
| Video Present | Derived from current ES evidence | Core channel | Yes | At least one expected video service evidence |
| Service Integrity Health | Expected SID + ES checks | Core channel | Yes | Expected-service state |
| RF Level | IRD observation where exposed | Core channel | Yes | Received RF level |
| SNR / C/N | IRD observation where exposed | Core channel | Yes | Signal quality |
| BER | IRD observation where exposed | Core channel | Yes | Bit error metric as exposed |
| Frequency | Config/device/web correlation | Core channel | Yes | Carrier identity |
| Symbol Rate | Config/device/web correlation | Core channel | Yes | Carrier identity |
| TS Bitrate | IRD observation where exposed | Core channel | Yes | Transport bitrate |
| TSID / NID / ONID | PSI/SI/device data | Core channels | Yes | Transport/network identity |
| Missing Services | Expected vs observed SIDs | Core channel | Yes | Expected SID absent |
| Unexpected Services | Observed vs expected SIDs | Core channel | Yes | Warning/inventory drift |
| ES Metadata Unavailable | Expected service ES check | Core channel | Yes | Service metadata integrity fault |
| Modulation / FEC | Structured device/web data where exposed | Status text | Yes | Configured/detected RF mode |
| ISI/MIS / PLS | Structured device/web data where exposed | Status text | Yes | Multistream/PLS detail |
| LNB / IF | Structured configuration where exposed | Status text | Yes | RF conversion context |
| Provider/network names | DVB/service metadata | Status text | Yes | Service/network context |
| Per-service SID/status/PID/stream type | Service/PMT/ES discovery | Selected service channels + status | Yes | Detailed service integrity |

No fabricated thresholds: This runbook does not assign universal RF, SNR or BER warning thresholds. Thresholds must be defined from link engineering, vendor specification and regulator policy. The project config template intentionally leaves such thresholds commented until operationally defined.

# 10. Phase F - SQLite persistence and 15-day history

The main production database is database\wisi_monitor.db. Core tables include chassis, modules, tuners, tuner_samples, ts_samples, pids, pid_samples, pcr_input_samples, pcr_pid_samples, transport_streams, services, service_streams, counter_state, monitoring_events and poll_runs. The services table uses service_id, not sid.

## 10.1 Dedicated TV43 history

| Table | Purpose |
| --- | --- |
| tv43_carrier_history | Rich per-carrier technical observation including lock, TS, integrity, RF/SNR/BER, tuning, IDs, bitrate, modulation/FEC, ISI/MIS, PLS, LNB/IF, counts and diagnostic text. |
| tv43_service_history | Per expected SID: name, present/running, ES/video availability, ES count, provider/status/detail. |
| tv43_history_meta | Retention/maintenance metadata. |

Retention is exactly 15 days; cleanup runs no more than once per day.

python .\validate_database.py

python .\validate_tv43_history.py

# Or point the validator at an explicit database:

python .\validate_tv43_history.py --database .\database\wisi_monitor.db

SQLite lock behavior: Concurrent PRTG sensor calls can contend for SQLite writes. V11.3J retries transient locks. If history persistence remains locked, a valid live PRTG payload is returned and the history-write failure is logged. Database lock contention is not a broadcast outage.

# 11. Phase G - PRTG integration

## 11.1 Why PRTG is viewer-only

PRTG displays the operational surface and historical channel graphs. It does not own the production transmission alarm state and it does not send production transmission email. This prevents PRTG channel-object quirks, stale limits or schema changes from redefining the regulatory alarm policy.

## 11.2 Wrapper installation

Production wrapper location on a standard PRTG installation:

C:\Program Files (x86)\PRTG Network Monitor\Custom Sensors\EXEXML\wisi_gt34_carrier.bat

The wrapper must invoke the server's actual Python executable and the permanent project copy of prtg_tv43_sensor.py. Never copy the old workstation's user-specific Python/Desktop paths unchanged.

# Direct sensor test from the project root

python .\prtg_tv43_sensor.py `

--host <CHASSIS_IP> `

--module <MODULE_NUMBER> `

--channel <LOGICAL_CHANNEL_NUMBER>

# Older logical-input sensor interface, useful for discovery validation

python .\prtg_sensor.py `

--config .\config.toml `

--host <CHASSIS_IP> `

--baseline .\baselines\baseline_<host>.toml `

--module <MODULE_NUMBER> `

--channel <LOGICAL_CHANNEL_NUMBER>

## 11.3 The 50-channel limit and the frozen 44-channel design

PRTG EXE/Script Advanced has a 50-channel maximum. PRTG also persists channel objects over time. Earlier dynamic schemas accumulated stale/duplicate channels; one historical sensor reached 58 registered channel objects, and stale channels could retain limits or become No Data/0. The production solution therefore returns a stable schema capped at 44 channels, leaving headroom below 50.

| Priority | Always-present core channels |
| --- | --- |
| 1-5 | Carrier / TS Health; Demod Lock; Transport Stream Present; Video Present; Service Integrity Health |
| 6-11 | RF Level; SNR; BER; Frequency; Symbol Rate; TS Bitrate |
| 12-17 | TSID; NID; ONID; Missing Services; Unexpected Services; ES Metadata Unavailable |
| After 17 | One service-health channel per authoritative SID where the frozen/historical PRTG schema includes it; then optional aggregates only while total remains <=44. |

All authoritative services remain covered by service-integrity logic even when a service does not receive its own PRTG channel. Extra detail is carried in the PRTG status/message and SQLite.

## 11.4 Rich status text

Full transponder information.

Configured/detected modulation and FEC.

PLS/ISI and LNB/IF where exposed.

Bitrate, RF level, SNR and BER.

Network/provider metadata.

Per-service SID, status, PID and stream-type detail.

Schema freeze: Do not dynamically add/remove PRTG channels during normal operation. If the authoritative service inventory changes, perform a controlled schema migration and keep the total <=44.

# 12. Phase H - service-integrity state model

| Observed condition | Result | Notification scope |
| --- | --- | --- |
| Carrier unlocked | FAULT | One immediate carrier-level email listing all expected multiplex services DOWN. |
| Carrier locked, TS absent | FAULT | One immediate carrier/TS email listing all expected multiplex services DOWN. |
| Carrier + TS healthy, expected SID missing | FAULT | Immediate email for only that failed expected service. |
| Carrier + TS healthy, expected SID present but ES metadata unavailable | FAULT | Immediate email for only that failed expected service. |
| Unexpected SID | WARNING/information | Not equivalent to expected-service failure. |
| Radio-only expected service with valid audio ES | May pass | Do not require every service to contain video. |
| Same fault remains active | Same episode | No repeated email. |
| Notified carrier/TS episode clears | RECOVERY | One email listing all recovered expected services UP. |
| Notified individual service episode clears | RECOVERY | One email for that service UP. |

For a TV-bearing carrier, at least one expected service currently has video evidence. This does not mean every service in the multiplex must have video.

# 13. Phase I - SMTP and approved email presentation

## 13.1 Secret handling

The sanitized project uses environment variables. Never place the SMTP password, PRTG passhash or other credentials in source control, documentation, screenshots or command transcripts.

# Example variable names only - enter real values locally on the server.

WISI_SMTP_HOST

WISI_SMTP_PORT

WISI_SMTP_USERNAME

WISI_SMTP_PASSWORD

WISI_EMAIL_FROM

WISI_EMAIL_TO

## 13.2 Trigger rules

No 60-second debounce. Alarm email is immediate at detection.

No repeated email while the same alarm episode remains active.

Recovery is immediate when a notified episode clears.

No severity field.

Email subject: Transmission Alert.

PRTG notification triggers are not used for production transmission email.

## 13.3 Approved V11.3L visual format

| DOWN email | Recovery email |
| --- | --- |
| Heading: Transmission Alert | Heading: Transmission Alert |
| Date/time stamp + separate PKT line | Date/time stamp + separate PKT line |
| Channel name | Channel name |
| Satellite name: Paksat MM1 | Satellite name: Paksat MM1 |
| Frequency band: C-band | Frequency band: C-band |
| Channel status: ❌ DOWN | Channel status: ✅ UP |
| No downtime row | Total downtime: HH:MM:SS |
| Emoji-sized PEMRA logo inline before italic automated-notification footer | Same footer |

The approved recovery layout does not add separate alarm-start/recovery-clear rows, a centered large logo, a separator line, or a severity field.

## 13.4 Safe presentation-only tests

python .\send_tv43_format_test.py

python .\send_tv43_format_test.py --recovery

# Optional test label:

python .\send_tv43_format_test.py --channel-name "TEST CHANNEL"

Do not use legacy stateful test: The old send_alarm_email_test.py depends on the legacy alarm_state model and is not the normal TV43 presentation test. The synthetic TV43 test must not create, clear, rearm or commission real alarm episodes.

# 14. Phase J - Windows production operation

Normal operation is Scheduled-Task driven. The two production tasks are WISI GT34 Monitor and WISI GT34 TV43 Alarm Policy. The alarm-policy task runs as SYSTEM at startup and evaluates snapshots at a 5-second interval; PRTG's final scan interval is 30 seconds.

## 14.1 Start/stop order

# Start: monitor first, alarm policy second

Start-ScheduledTask -TaskName "WISI GT34 Monitor"

Start-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

# Stop: alarm policy first, monitor second

Stop-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

Stop-ScheduledTask -TaskName "WISI GT34 Monitor"

# Check

Get-ScheduledTask -TaskName "WISI GT34 Monitor","WISI GT34 TV43 Alarm Policy" |

Select-Object TaskName,State

## 14.2 Planned maintenance

Disable-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

Disable-ScheduledTask -TaskName "WISI GT34 Monitor"

Stop-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

Stop-ScheduledTask -TaskName "WISI GT34 Monitor"

# Return to service

Enable-ScheduledTask -TaskName "WISI GT34 Monitor"

Enable-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

Start-ScheduledTask -TaskName "WISI GT34 Monitor"

Start-ScheduledTask -TaskName "WISI GT34 TV43 Alarm Policy"

# 15. From-scratch commissioning procedure

1. Freeze evidence: Save product documentation/MIB versions, firmware version, screenshots of module inventory and known carrier settings.

2. Network: Confirm chassis GUI reachability and actual SNMP response.

3. SNMP: Run module/service discovery; preserve raw/numeric evidence; do not invent unsupported OIDs.

4. Web structured data: Observe browser Network traffic for a known module/input/service and identify machine-readable resources.

5. Correlation: Prove one logical input using frequency/polarization/symbol-rate/service fingerprints and fail closed if ambiguous.

6. ES/PID: Run discover_streams on the known input and confirm expected SID/ES evidence.

7. Baseline: Generate a candidate baseline; review it manually against known operational configuration before approving.

8. One-carrier PRTG test: Run prtg_tv43_sensor.py directly; verify <=44 channels and rich status text.

9. SQLite: Run the sensor repeatedly and validate tv43 carrier/service history writes.

10. Service integrity: Verify expected SID missing/ES-N/A semantics without creating a real outage merely for testing.

11. Email presentation: Configure SMTP locally and use the synthetic TV43 DOWN/recovery format tests.

12. PRTG deployment: Deploy one stable sensor, then scale programmatically from the approved authoritative manifest. Do not manually create dozens of sensors.

13. Fleet validation: Run discovery/check tooling across configured IRDs and compare with the approved manifest.

14. Scheduled tasks: Create tasks with permanent server paths but keep alarm email suppressed until commissioning is complete.

15. Cutover: Start monitor first; validate snapshots/DB/PRTG; then enable alarm policy. When migrating from an existing system, stop old alarm policy first and transfer final state before new alarm policy starts.

# 16. Fleet validation commands

# Compare live fleet against approved service baselines.

python .\tools\check_fleet.py --config .\config.toml

# JSON output for machine inspection.

python .\tools\check_fleet.py --config .\config.toml --json

# Include informational findings.

python .\tools\check_fleet.py --config .\config.toml --include-info

# Read-only service-scope classification.

python .\tools\service_scope_report.py `

--config .\config.toml `

--manifest .\<APPROVED_MANIFEST.csv> `

--csv .\service_scope_report.csv

The fleet checker supports independent retries and concurrent IRD workers. Do not interpret a transient collection exception as a transmission outage; separate runtime/collection failure from broadcast state.

# 17. Troubleshooting decision tree

| Symptom | Check | Do not do |
| --- | --- | --- |
| MIB imports but useful fields are absent | Numeric walk; live values; GUI structured resources; product documentation. | Do not invent an OID from a GUI label. |
| GUI shows a value but SNMP does not | Inspect Network traffic and structured response; correlate to known input. | Do not screen-scrape the label as the authoritative model if structured data exists. |
| Logical input maps to wrong tuner | Check frequency/SR/SNR/RF/remote correlation and GUI logical identity. | Do not fall back to tuner_id = channel-1 unless the complete mapping criteria are satisfied. |
| Only tuner IDs 0-7 appear | Use the authoritative GUI/logical discovery path. | Do not assume eight is the logical-channel limit. |
| PRTG has >50/stale channels | Freeze schema; retire/rebuild under controlled migration; keep returned schema <=44. | Do not dynamically churn channels. |
| PRTG sensor Down after DB lock | Check live wrapper result and history-write diagnostic. | Do not classify SQLite contention as transmission failure. |
| Expected service present but ES-N/A | Treat as service-integrity metadata fault under current policy. | Do not claim decoded picture is black/off-air. |
| Unexpected SID appears | Record warning/inventory drift and investigate. | Do not automatically classify expected services as failed. |
| SMTP test fails | Check env vars, DNS/port/TLS/auth and recipient locally. | Do not print secrets into logs/chat. |
| Firmware/UI update breaks enrichment | Re-observe structured GUI requests and compare against known fingerprints. | Do not guess replacement endpoints/tags. |

# 18. Production-specific reference checkpoint

The following values describe the validated production fleet at V11.3L and are included so an engineer can distinguish a reproducible method from this particular deployment's inventory.

| Metric | Validated production value |
| --- | --- |
| WISI chassis | 4 |
| GT34 modules | 8 (physical slots M1 and M5 on each chassis) |
| Authoritative logical inputs discovered | 74 |
| Active TV-bearing carrier/multiplex inputs | 43 |
| DVB service instances in authoritative V6 | 168 |
| Final PRTG carrier sensors | 43 |
| PRTG returned-channel ceiling | 44 per sensor |
| PRTG scan interval | 30 seconds |
| TV43 SQLite retention | 15 days |
| Alarm-policy evaluation interval | 5 seconds |

Current production labels were WISI-IRD-01 through WISI-IRD-04. The production sensor IDs and IP addresses are installation-specific and must not be assumed on a fresh PRTG server.

# 19. Parameter evidence worksheet for a new IRD

Complete one row per parameter before declaring it production-supported.

| Parameter | Observed source | Raw field/OID/resource evidence | Unit/scaling proven? | Logical mapping proven? | PRTG/Status/DB decision |
| --- | --- | --- | --- | --- | --- |
| Demod lock |  |  |  |  |  |
| RF level |  |  |  |  |  |
| SNR/CN |  |  |  |  |  |
| BER |  |  |  |  |  |
| Frequency |  |  |  |  |  |
| Symbol rate |  |  |  |  |  |
| Modulation/FEC |  |  |  |  |  |
| ISI/MIS/PLS |  |  |  |  |  |
| TS presence/bitrate |  |  |  |  |  |
| TSID/NID/ONID |  |  |  |  |  |
| SID/service name |  |  |  |  |  |
| PID/ES stream type |  |  |  |  |  |

# 20. Evidence log for web-command/resource discovery

| Date/firmware | GUI action | Request method/path (redacted) | Response field(s) | Known carrier fingerprint | Conclusion/confidence |
| --- | --- | --- | --- | --- | --- |

Security: Do not place passwords, session cookies, authorization headers, SNMP community strings, SMTP secrets, or PRTG passhashes in this worksheet.

# 21. Acceptance checklist

☐ All chassis/GT34 modules are identified and reachable.

☐ SNMP behavior is evidenced; MIB limitations are recorded.

☐ Structured web acquisition is evidenced for the deployed firmware.

☐ Every production logical carrier is deterministically mapped.

☐ Every expected service is SID-based and reviewed.

☐ TV-bearing classification uses explicit ES/video evidence, not names.

☐ PRTG sensor output is stable and never exceeds 44 live channels.

☐ 17 core PRTG channels are present where the underlying data is available.

☐ Overflow technical/service detail is visible in status text and retained in SQLite.

☐ TV43 carrier and service history validates and 15-day retention is configured.

☐ SQLite contention does not create false transmission alarms.

☐ PRTG notification triggers are not used for production transmission email.

☐ SMTP secrets are stored outside source/documentation.

☐ Synthetic DOWN and recovery email formats match the approved V11.3L presentation.

☐ Alarm state machine performs immediate notification, duplicate suppression and immediate recovery.

☐ Scheduled Tasks use permanent server paths and correct start/stop order.

☐ A final commissioning record captures versions, manifests, validation outputs and known limitations.

# 22. Non-negotiable engineering rules

Do not fabricate OIDs, endpoints, tags, enum meanings, units, thresholds, logical mappings or service states.

Do not equate a GUI logical input with a low-level tuner index without deterministic evidence.

Do not infer TV/radio from a service name.

Do not require every DVB service in a multiplex to contain video.

Do not state that ES-N/A proves black/off-air decoded video.

Do not exceed 44 live PRTG channels in the frozen production presentation.

Do not use PRTG notification triggers for production transmission email.

Do not treat application/database errors as broadcast outages.

Do not expose SMTP secrets, SNMP communities or PRTG passhashes.

Do not silently change the frozen alarm semantics: immediate detection, no debounce, episode suppression, immediate recovery, no severity field.

# 23. Source-of-truth files in the project

| File/folder | Use |
| --- | --- |
| gt34_monitor/ | Core structured SNMP/web discovery and polling package. |
| tools/discover_modules.py | Physical module inventory. |
| tools/discover_services.py | GT34 service discovery and candidate baseline. |
| tools/discover_streams.py | Service ES/PID discovery. |
| tools/discover_fleet.py | Configured fleet discovery. |
| tools/check_fleet.py | Live fleet versus approved baseline. |
| gt34_monitor/webstatus.py | Fail-closed web enrichment/mapping. |
| gt34_monitor/fastpath.py | Fast live acquisition/enrichment. |
| prtg_tv43_sensor.py | Final bounded authoritative carrier sensor. |
| tv43_history.py / validate_tv43_history.py | 15-day carrier/service persistence and validation. |
| tv43_alarm_policy_final.py | Final episode-based alarm/recovery policy and approved renderer. |
| email_notifier.py | SMTP sending layer. |
| send_tv43_format_test.py | Safe synthetic presentation test. |
| authoritative_inventory_v6/ | Validated production logical/service inventory. |
| state/tv43_alarm_snapshots/ | Current TV43 snapshots consumed by alarm policy. |
| database/tv43_alarm_policy.sqlite3 | Alarm episode/suppression/recovery state. |
| database/wisi_monitor.db | Main telemetry/history database. |

# 24. Final engineering principle

A new engineer should be able to reproduce the method without reproducing undocumented assumptions. The correct result of a discovery step can be 'not exposed', 'ambiguous', or 'metadata unavailable'. Those are valid engineering outcomes. A fabricated OID, guessed endpoint, arbitrary tuner assignment, inferred service type, or invented threshold is not.

The deployment is considered reproducible only when each production parameter has a traceable evidence source, each logical carrier/service identity is deterministic, the PRTG surface is bounded and stable, SQLite history is validated, and alarm/email behavior is independently controlled by Python.